## Asset
Asset Naming Convention
Client/SiteID/PlantID/system/DeviceCat_ID/measurement
SCTL/DRBE090/PL01/SYS01/INVR_AB8783/TmpCab
Device Categories | Meaning
INVR | Inverter
LOGG | Logger
PMTR | Power Meter
EMS | Energy Management System
EVSE | Electric Vechckle Charger Socket
BESS | Battery Energy Storage System
MEAS | Measurment
RIO | Remote Input / Output

## Models
Model 101: Single-phase Inverter
Model 102: Split-phase Inverter
Model 103: Three-phase Inverter
Model 120: Inverter Controls Nameplate Ratings
Model 121: Inverter Controls Basic Settings
Model 122: Inverter Controls Extended Measurements and Status
Model 123: Immediate Inverter Controls
Model 124: Basic Storage Controls
Model 203: Three-Phase Wye (abcn) meter
Model 302: Irradiance
Model 307: Base Meteorological Model
Model 802: Battery Base Model

## 101
SunSpec Name | Unit | Description
ID | - | Model identifier
L | registers | Model length
A | A | AC Current
AphA | A | Phase A Current
AphB | A | Phase B Current
AphC | A | Phase C Current
A_SF | - | Scale factor for current
PPVphAB | V | Phase Voltage AB
PPVphBC | V | Phase Voltage BC
PPVphCA | V | Phase Voltage CA
PhVphA | V | Phase Voltage AN
PhVphB | V | Phase Voltage BN
PhVphC | V | Phase Voltage CN
V_SF | - | Scale factor for voltage
W | W | AC Power
W_SF | - | Scale factor for power
Hz | Hz | Line Frequency
Hz_SF | - | Scale factor for frequency
VA | VA | AC Apparent Power
VA_SF | - | Scale factor for apparent power
VAr | var | AC Reactive Power
VAr_SF | - | Scale factor for reactive power
PF | Pct | AC Power Factor
PF_SF | - | Scale factor for power factor
WH | Wh | AC Energy
WH_SF | - | Scale factor for energy
DCA | A | DC Current
DCA_SF | - | Scale factor for DC current
DCV | V | DC Voltage
DCV_SF | - | Scale factor for DC voltage
DCW | W | DC Power
DCW_SF | - | Scale factor for DC power
TmpCab | C | Cabinet Temperature
TmpSnk | C | Heat Sink Temperature
TmpTrns | C | Transformer Temperature
TmpOt | C | Other Temperature
Tmp_SF | - | Scale factor for temperature
St | - | Enumerated value. Operating state
StVnd | - | Vendor specific operating state code
Evt1 | - | Bitmask value. Event fields
Evt2 | - | Reserved for future use
EvtVnd1 | - | Vendor defined events
EvtVnd2 | - | Vendor defined events
EvtVnd3 | - | Vendor defined events
EvtVnd4 | - | Vendor defined events

## 102
SunSpec Name | Unit | Description
A | Amps | AC Total Current
A_SF | - | AC Current Scale Factor
PhV | Volts | AC Voltage (L-N)
PhV_SF | - | AC Voltage Scale Factor
PhVAB | Volts | AC Voltage (L1-L2)
W | Watts | AC Power
W_SF | - | AC Power Scale Factor
Hz | Hertz | AC Frequency
Hz_SF | - | AC Frequency Scale Factor
VA | Volt-Amps | Apparent Power
VA_SF | - | Apparent Power Scale Factor
VAr | VAr | Reactive Power
VAr_SF | - | Reactive Power Scale Factor
PF | % | Power Factor
PF_SF | - | Power Factor Scale Factor
WH | Watt-Hours | Energy Output
WH_SF | - | Energy Output Scale Factor
DCA | Amps | DC Current
DCA_SF | - | DC Current Scale Factor
DCV | Volts | DC Voltage
DCV_SF | - | DC Voltage Scale Factor
DCW | Watts | DC Power

## 103
SunSpec Name | Unit | Description
A | Amps | AC Current
AphA | Amps | Phase A Current
AphB | Amps | Phase B Current
AphC | Amps | Phase C Current
A_SF | - | AC Current Scale Factor
PhVphA | Volts | Phase A Voltage
PhVphB | Volts | Phase B Voltage
PhVphC | Volts | Phase C Voltage
PhV_SF | - | AC Voltage Scale Factor
W | Watts | AC Power
W_SF | - | AC Power Scale Factor
Hz | Hertz | AC Frequency
Hz_SF | - | AC Frequency Scale Factor
VA | Volt-Amps | Apparent Power
VA_SF | - | Apparent Power Scale Factor
VAr | VAr | Reactive Power
VAr_SF | - | Reactive Power Scale Factor
PF | % | Power Factor
PF_SF | - | Power Factor Scale Factor
WH | Watt-Hours | Energy Output Accumnaltive
WHD | Watt-Hours | Energy Output Daily
WHM | Watt-Hours | Energy Output Monthly
WH_SF | - | Energy Output Scale Factor
TRT |  | Total Running Time
DCA | Amps | DC Current
DCA_SF | - | DC Current Scale Factor
DCV | Volts | DC Voltage
DCV_SF | - | DC Voltage Scale Factor
DCW | Watts | DC Power
DCW_SF | - | DC Power Scale Factor
TmpCab | °C | Cabinet Temperature
TmpSnk | °C | Heat Sink Temperature
TmpTrns | °C | Transformer Temperature
TmpOt | °C | Other Temperature
St | - | Operating State
StVnd | - | Vendor Operating State
Evt1 | - | Event Flags 1
Evt2 | - | Event Flags 2
EvtVnd1 | - | Vendor Event Flags 1
EvtVnd2 | - | Vendor Event Flags 2
EvtVnd3 | - | Vendor Event Flags 3
EvtVnd4 | - | Vendor Event Flags 4

## 120
SunSpec Name | Unit | Description
ID | - | Model identifier
L | registers | Model length
DERTyp | - | Type of DER device. Default value is 4 to indicate PV device.
WRtg | W | Continuous power output capability of the inverter.
VARtg | VA | Continuous Volt-Ampere capability of the inverter.
VArRtgQ1 | VAr | Continuous VAR capability of the inverter in quadrant 1.
VArRtgQ2 | VAr | Continuous VAR capability of the inverter in quadrant 2.
VArRtgQ3 | VAr | Continuous VAR capability of the inverter in quadrant 3.
VArRtgQ4 | VAr | Continuous VAR capability of the inverter in quadrant 4.
ARtg | A | Maximum RMS AC current level capability of the inverter.
PFRtgQ1 | cos() | Minimum power factor capability of the inverter in quadrant 1.
PFRtgQ2 | cos() | Minimum power factor capability of the inverter in quadrant 2.
PFRtgQ3 | cos() | Minimum power factor capability of the inverter in quadrant 3.
PFRtgQ4 | cos() | Minimum power factor capability of the inverter in quadrant 4.
WHRtg | Wh | Nominal energy rating of storage device.
AhrRtg | AH | The usable capacity of the battery.
MaxChaRte | W | Maximum rate of energy transfer into the storage device.
MaxDisChaRte | W | Maximum rate of energy transfer out of the storage device.

## 121
SunSpec Name | Unit | Description
ID | - | Model Identifier
L | registers | Model Length
WMax | W | Maximum Power Output
VRef | V | Point of Common Coupling Voltage
VRefOfs | V | Voltage Offset
VMax | V | Maximum Voltage Setpoint
VMin | V | Minimum Voltage Setpoint
VAMax | VA | Maximum Apparent Power Setpoint
VArMaxQ1 | var | Maximum Reactive Power Q1
VArMaxQ2 | var | Maximum Reactive Power Q2
VArMaxQ3 | var | Maximum Reactive Power Q3
VArMaxQ4 | var | Maximum Reactive Power Q4
WGra | % WMax/sec | Active Power Ramp Rate
PFMinQ1 | cos() | Minimum Power Factor Q1
PFMinQ2 | cos() | Minimum Power Factor Q2
PFMinQ3 | cos() | Minimum Power Factor Q3
PFMinQ4 | cos() | Minimum Power Factor Q4
VArAct | - | VAR Action on Charge/Discharge
ClcTotVA | - | Total Apparent Power Calculation Method
MaxRmpRte | % WGra | Maximum Ramp Rate Setpoint
ECPNomHz | Hz | Nominal Frequency Setpoint
ConnPh | - | Connected Phase Identity
WMax_SF | - | Scale Factor for Real Power
VRef_SF | - | Scale Factor for PCC Voltage
VRefOfs_SF | - | Scale Factor for Offset Voltage
VMinMax_SF | - | Scale Factor for Min/Max Voltage
VAMax_SF | - | Scale Factor for Apparent Power
VArMax_SF | - | Scale Factor for Reactive Power
WGra_SF | - | Scale Factor for Ramp Rate
PFMin_SF | - | Scale Factor for Min Power Factor
MaxRmpRte_SF | - | Scale Factor for Max Ramp Rate
ECPNomHz_SF | - | Scale Factor for Nominal Frequency

## 122
SunSpec Name | Unit | Description
ID | - | Model identifier
L | registers | Model length
PVConn | - | PV inverter present/available status.
StorConn | - | Storage inverter present/available status.
ECPConn | - | ECP connection status: disconnected=0 connected=1.
ActWh | Wh | AC lifetime active (real) energy output.
ActVAh | VAh | AC lifetime apparent energy output.
ActVArhQ1 | varh | AC lifetime reactive energy output in quadrant 1.
ActVArhQ2 | varh | AC lifetime reactive energy output in quadrant 2.
ActVArhQ3 | varh | AC lifetime negative energy output in quadrant 3.
ActVArhQ4 | varh | AC lifetime reactive energy output in quadrant 4.
VArAval | var | Amount of VARs available without impacting watts output.
VArAval_SF | - | Scale factor for available VARs.
WAval | var | Amount of Watts available.
WAval_SF | - | Scale factor for available Watts.
StSetLimMsk | - | Bit Mask indicating setpoint limit(s) reached.
StActCtl | - | Bit Mask indicating which inverter controls are currently active.
TmSrc | - | Source of time synchronization.
Tms | Secs | Seconds since 01-01-2000 00:00 UTC.
RtSt | - | Bit Mask indicating active ride-through status.
Ris | ohms | Isolation resistance.
Ris_SF | - | Scale factor for isolation resistance.

## 123
SunSpec Name | Unit | Description
ID | - | Model identifier
L | registers | Model length
Conn_WinTms | Seconds | Time window for connect/disconnect.
Conn_RvrtTms | Seconds | Timeout period for connect/disconnect.
Conn | - | Enumerated valued. Connection control.
WMaxLimPct | % WMax | Set power output to specified level.
WMaxLimPct_WinTms | Seconds | Time window for power limit change.
WMaxLimPct_RvrtTms | Seconds | Timeout period for power limit.
WMaxLimPct_RmpTms | Seconds | Ramp time for moving from current setpoint to new setpoint.
WMaxLimEna | - | Enumerated valued. Throttle enable/disable control.
OutPFSet_Ena | - | Enumerated valued. Fixed power factor enable/disable control.
OutPFSet | cos() | Set power factor to specific value - cosine of angle.
OutPFSet_WinTms | Seconds | Time window for power factor change.
OutPFSet_RvrtTms | Seconds | Timeout period for power factor.
OutPFSet_RmpTms | Seconds | Ramp time for moving from current setpoint to new setpoint.
VArWMaxPct | % WMax | Reactive power in percent of WMax.
VArMaxPct | % VArMax | Reactive power in percent of VArMax.
VArAvalPct | % VArAval | Reactive power in percent of VArAval.
VArPct_WinTms | Seconds | Time window for VAR limit change.
VArPct_RvrtTms | Seconds | Timeout period for VAR limit.
VArPct_RmpTms | Seconds | Ramp time for moving from current setpoint to new setpoint.
VArPct_Mod | - | Enumerated value. VAR percent limit mode.
VArPct_Ena | - | Enumerated valued. Percent limit VAr enable/disable control.
WMaxLimPct_SF | - | Scale factor for power output percent.
OutPFSet_SF | - | Scale factor for power factor.
VArPct_SF | - | Scale factor for reactive power percent.

## 124
SunSpec Name | Unit | Description
ID | - | Model Identifier
L | registers | Model Length
ChaSt | - | Charge Status
ChaStVnd | - | Vendor Charge Status
InBatV | V | Internal Battery Voltage
ChaMaxW | W | Maximum Charge Power
ChaMaxVAr | VAr | Maximum Charge Reactive Power
ChaMaxA | A | Maximum Charge Current
DisChaMaxW | W | Maximum Discharge Power
DisChaMaxVAr | VAr | Maximum Discharge Reactive Power
DisChaMaxA | A | Maximum Discharge Current
StorCtl_Mod | - | Storage Control Mode
ChaCtl | - | Charge Control
DisChaCtl | - | Discharge Control
StorCtl_Mod_SF | - | Scale Factor for Storage Control Mode
InBatV_SF | - | Scale Factor for Internal Battery Voltage
ChaMaxW_SF | - | Scale Factor for Maximum Charge Power
ChaMaxVAr_SF | - | Scale Factor for Maximum Charge Reactive Power
ChaMaxA_SF | - | Scale Factor for Maximum Charge Current
DisChaMaxW_SF | - | Scale Factor for Maximum Discharge Power
DisChaMaxVAr_SF | - | Scale Factor for Maximum Discharge Reactive Power
DisChaMaxA_SF | - | Scale Factor for Maximum Discharge Current

## 203
SunSpec Name | Unit | Description
ID | - | Model identifier
L | registers | Model length
A | A | Total AC Current
AphA | A | Phase A Current
AphB | A | Phase B Current
AphC | A | Phase C Current
A_SF | - | Current scale factor
PhV | V | Line to Neutral AC Voltage
PhVphA | V | Phase Voltage AN
PhVphB | V | Phase Voltage BN
PhVphC | V | Phase Voltage CN
PPV | V | Line to Line AC Voltage
PhVphAB | V | Phase Voltage AB
PhVphBC | V | Phase Voltage BC
PhVphCA | V | Phase Voltage CA
V_SF | - | Voltage scale factor
Hz | Hz | Frequency
Hz_SF | - | Frequency scale factor
W | W | Total Real Power
WphA | W | Watts phase A
WphB | W | Watts phase B
WphC | W | Watts phase C
W_SF | - | Real Power scale factor
VA | VA | AC Apparent Power
VAphA | VA | VA phase A
VAphB | VA | VA phase B
VAphC | VA | VA phase C
VA_SF | - | Apparent Power scale factor
VAR | var | Reactive Power
VARphA | var | VAR phase A
VARphB | var | VAR phase B
VARphC | var | VAR phase C
VAR_SF | - | Reactive Power scale factor
PF | Pct | Power Factor
PFphA | Pct | PF phase A
PFphB | Pct | PF phase B
PFphC | Pct | PF phase C
PF_SF | - | Power Factor scale factor
TotWhExp | Wh | Total Real Energy Exported
TotWhExpPhA | Wh | Total Watt-hours Exported phase A
TotWhExpPhB | Wh | Total Watt-hours Exported phase B
TotWhExpPhC | Wh | Total Watt-hours Exported phase C
TotWhImp | Wh | Total Real Energy Imported
TotWhImpPhA | Wh | Total Watt-hours Imported phase A
TotWhImpPhB | Wh | Total Watt-hours Imported phase B
TotWhImpPhC | Wh | Total Watt-hours Imported phase C
TotWh_SF | - | Real Energy scale factor
TotVAhExp | VAh | Total Apparent Energy Exported
TotVAhExpPhA | VAh | Total VA-hours Exported phase A
TotVAhExpPhB | VAh | Total VA-hours Exported phase B
TotVAhExpPhC | VAh | Total VA-hours Exported phase C
TotVAhImp | VAh | Total Apparent Energy Imported
TotVAhImpPhA | VAh | Total VA-hours Imported phase A
TotVAhImpPhB | VAh | Total VA-hours Imported phase B
TotVAhImpPhC | VAh | Total VA-hours Imported phase C
TotVAh_SF | - | Apparent Energy scale factor
Evt | - | Meter Event Flags

## 302
SunSpec Name | Unit | Description
ID | - | Model identifier
L | registers | Model length
GHI | W/m2 | Global Horizontal Irradiance
POAI | W/m2 | Plane-of-Array Irradiance
DFI | W/m2 | Diffuse Irradiance
DNI | W/m2 | Direct Normal Irradiance
OTI | W/m2 | Other Irradiance

## 307
SunSpec Name | Unit | Description
ID | - | Model identifier
L | registers | Model length
TmpAmb | C | Ambient Temperature
RH | Pct | Relative Humidity
Pres | HPa | Barometric Pressure
WndSpd | mps | Wind Speed
WndDir | deg | Wind Direction
Rain | mm | Rainfall
Snw | mm | Snow Depth
PPT | - | Precipitation Type (WMO 4680 SYNOP code reference)
ElecFld | Vm | Electric Field
SurWet | kO | Surface Wetness
SoilWet | Pct | Soil Wetness

## 802
SunSpec Name | Unit | Description
ID | - | Model identifier
L | - | Model length
AHRtg | registers | Nameplate charge capacity in amp-hours.
WHRtg | Ah | Nameplate energy capacity in DC watt-hours.
WChaRteMax | Wh | Maximum rate of energy transfer into the storage device in DC watts.
WDisChaRteMax | W | Maximum rate of energy transfer out of the storage device in DC watts.
DisChaRte | W | Self discharge rate. Percentage of capacity discharged per day.
SoCMax | %WHRtg | Manufacturer maximum state of charge, expressed as a percentage.
SoCMin | %WHRtg | Manufacturer minimum state of charge, expressed as a percentage.
SocRsvMax | %WHRtg | Setpoint for maximum reserve for storage as a percentage.
SoCRsvMin | %WHRtg | Setpoint for minimum reserve for storage as a percentage.
SoC | %WHRtg | State of charge, expressed as a percentage.
DoD | %WHRtg | Depth of discharge, expressed as a percentage.
SoH | % | Percentage of battery life remaining.
NCyc | % | Number of cycles executed in the battery.
ChaSt | - | Charge status of storage device.
LocRemCtl | - | Battery control mode.
Hb | - | Value incremented every second with periodic resets to zero.
CtrlHb | - | Value incremented every second with periodic resets to zero.
AlmRst | - | Used to reset any latched alarms.
Typ | - | Type of battery.
State | - | State of the battery bank.
StateVnd | - | Vendor specific battery bank state.
WarrDt | - | Date the device warranty expires.
Evt1 | - | Alarms and warnings. Bit flags.
Evt2 | - | Alarms and warnings. Bit flags.
EvtVnd1 | - | Vendor defined events.
EvtVnd2 | - | Vendor defined events.
V | - | DC Bus Voltage.
VMax | V | Instantaneous maximum battery voltage.
VMin | V | Instantaneous minimum battery voltage.
CellVMax | V | Maximum voltage for all cells in the bank.
CellVMaxStr | V | String containing the cell with maximum voltage.
CellVMaxMod | - | Module containing the cell with maximum voltage.
CellVMin | - | Minimum voltage for all cells in the bank.
CellVMinStr | V | String containing the cell with minimum voltage.
CellVMinMod | - | Module containing the cell with minimum voltage.
CellVAvg | - | Average cell voltage for all cells in the bank.
A | V | Total DC current flowing to/from the battery bank.
AChaMax | A | Instantaneous maximum DC charge current.
ADisChaMax | A | Instantaneous maximum DC discharge current.
W | A | Total power flowing to/from the battery bank.
ReqInvState | W | Request from battery to start or stop the inverter.
ReqW | - | AC Power requested by battery.
SetOp | W | Instruct the battery bank to perform an operation.
SetInvState | - | Set the current state of the inverter.
AHRtg_SF | - | Scale factor for charge capacity.
WHRtg_SF | - | Scale factor for energy capacity.
WChaDisChaMax_SF | - | Scale factor for max charge/discharge rate.
DisChaRte_SF | - | Scale factor for self discharge rate.
SoC_SF | - | Scale factor for state of charge values.
DoD_SF | - | Scale factor for depth of discharge.
SoH_SF | - | Scale factor for state of health.
V_SF | - | Scale factor for DC bus voltage.
CellV_SF | - | Scale factor for cell voltage.
A_SF | - | Scale factor for DC current.
AMax_SF | - | Scale factor for instantaneous charge/discharge current.
W_SF | - | Scale factor for AC power request.